Title Page

| Number | Item | Information |
| --- | --- | --- |
| 1 | Article title | Enhancing Resilience by Reducing Critical Load Loss via an Emergent Trading Framework Considering Possible Resources Isolation Under Typhoon |
| 2 | Running head/short title | None |
| 3 | Names of all authors in the same order as mentioned in ScholarOne | Yingjun Wu Chengjun Liu Zhiwei Lin Yingtao Ru Tao Huang |
| 4 | Author’s contribution | Wu Yingjun: Conceptualization, Methodology, Supervision, Writing – review & editing Chengjun Liu: Data curation, Formal analysis, Methodology, Writing – original draft Zhiwei Lin: Reources, Software, Visualization Ru Yingtao: Data curation, Writing – original draft Tao Huang: Supervision, Writing – review & editing |
| 5 | Affiliation of all authors | Yingjun Wu, Chengjun Liu, Zhiwei Lin , Yingtao Ru, are with College of Energy and Electrical Engineering, Hohai University, Nanjing, China Tao Huang is with the Department of Energy, Politecnico di Torino, Italy. |
| 6 | Postal and E-mail address of the corresponding author | yingjunwu@hotmail.com |
| 7 | Funding information | None |
| 8 | Conflict of Interest statement | The authors declared that they have no conflicts of interest to this work |
| 9 | Permission to reproduce materials from other sources | None |
| 10 | Data Availability statement | The data that support the findings of this study are available on request from the corresponding author. The data are not publicly available due to privacy or ethical restrictions |

Enhancing Resilience by Reducing Critical Load Loss via an Emergent Trading Framework Considering Possible Resources Isolation Under Typhoon

Yingjun Wu 1*, Chengjun Liu 1, Zhiwei Lin 1, Yingtao Ru1, Tao Huang 2

1 Department of Electrical Engineering, College of Energy and Electrical Engineering, Hohai University, Nanjing, China

2 Department of Energy, Politecnico di Torino, Italy and Xihua University, China

* yingjunwu@hotmail.com

Abstract: Natural disasters have posed great challenges to the power system in recent years. This paper proposes an emergent trading framework that uses parking lots as resources to provide power support to critical loads in a blackout due to typhoon. Firstly, a distribution line fault model under typhoon is established to create possible fault scenarios with the typhoon trajectory data. Subsequently, an evolutionary Stackelberg game-based trading model is proposed to maximize all stakeholders’ economic benefits while reducing the critical load loss for all chosen scenarios, leading to enhanced system resilience. At the same time, a benefit allocation mechanism and free-riding penalty are incorporated in the framework to motivate players’ participation while limiting the negative effect of free-riders. Further, an iterative evolutionary-Stackelberg solution set-up is applied to obtain the equilibria of the proposed framework. Finally, a modified IEEE 69-bus system is used to illustrate and validate the proposed framework.

- Nomenclature

| Sets and Indexes |  |  |
| --- | --- | --- |
| i / j / l | Index for CL/PL/EV, |  |
| s | Index for scenario, |  |
| t | Index for time, |  |
| {}/{} | Set of CL/PL bidding strategy |  |
| c | Index for distribution line, |  |
| Superscript and Subscript |  |  |
| •c | Corresponding parameter • of distribution line, including tower (ton) and conductor (con) |  |
| •t | Corresponding • parameter at time t |  |
| •typh | Corresponding • parameter of typhoon |  |
| •i /•j | Corresponding parameter • of CLi /PLj |  |
| •l,j | Corresponding parameter • of Electric vehicle l in PLj |  |
| •t,s | Corresponding parameter • in scenario s at time t |  |
| •min /•max | Maximum/minimum (limits) of corresponding quantity • |  |
| •C /•D | Parameter • in charge/discharge situation |  |
| Parameters |  |  |
| V | Speed of typhoon |  |
| R | Radius |  |
| Z | Vertical distance from the typhoon center |  |
| A, B, randC | Typhoon-related constants |  |
| S | Component strength standard deviation |  |
|  | Component strength average |  |
| / | Stress/bending moment |  |
|  | Average stress/bending moment |  |
| L | Force load |  |
| H | Height |  |
|  | Angle of wind direction and component |  |
|  | Recovery rate |  |
| E | Information entropy |  |
| cCL/cPL/cDU |  | Objective function of CL/PL/DU |
|  | Occurrence probability |  |
| / | Benefit allocation coefficient |  |
| D, E, F | Constants related to CL |  |
| closs | The damage function |  |
| pi0 | Load loss before purchasing power |  |
| I | Evaluation Indicator |  |
| RI | Resilience Index |  |
|  | The revised damage function |  |
| cbuy | Power purchase cost |  |
|  | Free-riding penalty coefficient |  |
| Pbuy/Psell | Price of buying/selling power |  |
| cres | The resource cost function |  |
|  | The revised resource cost function |  |
|  | Benefit allocation coefficient |  |
| bsell | Benefits of selling power |  |
| G, H | Constants related to PL |  |
| SOC | State of charge |  |
| R | Power of charging or discharging |  |
|  | Efficiency |  |
| N | Number |  |
| V | Capacity |  |
| U | Voltage |  |
| Variables |  |  |
| v | Wind speed |  |
| r | Distance from typhoon center |  |
|  | Fault rate |  |
| q | Binary variable of distribution line (1 = fault, 0= otherwise) |  |
| p | Expected load loss |  |
|  | CL bidding strategy |  |
| r | Expected power selling |  |
|  | PL bidding strategy |  |
| u | Binary variable of the status of PLj (1 = installed, 0= otherwise) |  |

Introduction

Frequent natural disasters have exposed the vulnerability of the power system under unpredictable extreme weather in recent years [1]-[4], which could lead to a large-scale and long-playing outage of the power system. In this context, not only the reliability of the power system in the conventional sense needs to be improved, but also the resilience of the entire distribution network (DN) needs to be enhanced.

To analyse the impact of extreme weather on the power system, it is necessary to classify and model extreme weather [5]. As one of the most frequent happening extreme weather, the wind hazard has been studied by scholars for many years [6]-[10]. Reference [7] analyses the impact of a hurricane on a real power system, and proposes a hurricane modeling approach. Reference [8] models wind storms and analyse their impact on the DN in the northeast U.S. Reference [9] proposes a probabilistic typhoon model and assesses the impact on transmission systems. Reference [10] analyses the effect of typhoon track uncertainty on power system lines. Obviously， wind hazards, as one of the most frequent and high destructive natural hazards, should be prioritized in the consideration for the improvement of the power system resilience.

In the context of power systems, resilience could be defined as the grid’s ability to withstand extraordinary and high-impact low-probability events [11]. Power system resilience covers the entire process from grid preparation before a disaster, emergency operation during a disaster, and rapid recovery after a disaster. The development of the Smart Grid brings higher flexibility, security, and self-healing capacity. Especially, distributed energy resources bring more flexible and effective fault response strategies to the power system and make it possible to actively improve the resilience of the DN. The rapid restoration of power supply in the DN after a disaster is a research hotspot [12], [13]. The rapid restoration operation utilizes novel technologies to leverage existing distributed energy resources in the DN to defend the system or reduce the disastrous consequence. Due to its flexibility and wide distribution, electric vehicle (EV) is usually considered as a recovery resource after hazards [14]. References [15]-[17] propose some strategies to achieve rapid power restoration with EVs. References [18], [19] respectively optimizes the location of parking lots (PLs) and electric buses to prevent the harm the disaster brings. Reference [20] focuses on the optimization of the Vehicle-to-Home problem during a power blackout. Reference [21] presents a two-stage framework of rapid power recovery with the utilization of distributed resources including EVs. In summary, EVs have a place in researches on DN resilience enhancement and can be used as a quick power recovery resource during an outage. Yet, when considering rapid power restoration by using EVs, references [15], [16], [18], [19], and [20] do not consider the availability of the EVs as well as the locations where the fault occurred. However, faults at different locations in the DN may result in very different outcomes, and it is important to take this into account in the power load recovery. Further, many studies, including the above-mentioned ones, directly dispatch EVs in an outage due to a disaster. However, most EVs do not belong to the DN. Therefore, if the economic benefits of the EV owners cannot be guaranteed, their willingness of participating in the power recovery will decrease.

Therefore, a reasonable market mechanism could significantly increase resource owners’ willingness to cooperate with the DN [22]-[24]. Market approaches can be also effective in emergency conditions; the emergency demand response program for large load users (non-distributed resource) is an example in point [25]-[27]. Reference [25] presents a demand response program that could maintain the system’s reliability during the emergency period. Reference [26] uses Nash bargaining theory to design an incentive mechanism in emergency demand response for data centers. In [27], an emergency demand response program is designed to improve short-term voltage stability. These large loads themselves are much vulnerable to disaster than distributed resources; thus they cannot provide flexibility when the system needs. Therefore, it is more suitable to consider distributed resources as quick power recovery resources. Yet, due to their distributed and small-scale natures, a specifically designed market instrument is absolutely needed to effectively stimulate their participation in this process. Therefore, this paper proposes an emergent trading framework to encourage their participation to enhance the system's resilience.

It should be noted that market-based instruments may lead to free-riding behavior among the critical load users who buy the resilience enhancement services in the market, especially in the DN due to its topological features. Such free-riding behavior has been studied in the traditional distribution power reliability [28] in normal situations. Not to mention that free-riders may cause greater harm under emergency. To overcome this issue, this paper introduces a penalty to reduce its impact.

This paper proposes a market-based framework applied to emergent or extreme situations by using PLs as a quick recovery resource to reduce critical load loss and improve the resilience of the entire DN during a typhoon crossing. Under the framework, the mathematical model for the typhoon is firstly built, and a DN fault scenario formation method is proposed against the typhoon. Then an evolutionary Stackelberg game-based trading model is established to consider maximizing all stakeholders’ economic benefits and reducing the load loss. In this model, critical loads (CLs) could reduce their load loss in typhoon weather, PLs could receive adequate compensation and rewards to stimulate them to participate in the transaction, and distribution utility (DU) could ensure its economic benefits and enhance the DN resilience through the trading. A benefit allocation mechanism is proposed for all stakeholders to motivate all stakeholders to participate in the trading.

Contributions of this paper are as follows:

1) This paper proposes an emergent trading framework which can be used to supplement normal market under emergent or extreme situation, such as adverse event or extreme weather conditions. Under the framework, the PLs are stimulated to participate in the trading which could potentially help the CLs to decrease the loss, resulting in an increase of the DN resilience.

2) Further, an evolutionary Stackelberg game with three stakeholders is proposed for obtaining the evolutionary equilibria under the proposed emergent trading framework. Besides considering the economic benefits of the PLs and CLs, the proposed game includes a cost and benefit allocation mechanism to ensure more economic benefits for the DU than usual circumstances, thus motivating the DU to facilitate the trading.

3) The proposed framework considers the negative effect of free-riders on trading by applying the free-riding penalty.

4) Different distribution network topologies may result from faults at different locations and different periods. Thus, a formation method for the most likely fault scenarios based on the typhoon model and the information entropy constraint is proposed. Further, the resilience enhancement framework is based on selected scenarios.

The rest of this paper is organized as follows. In Section 2, the problem under study is described. The mathematical formulation is presented in Section 3. The solution algorithm is discussed in Section 4. The case study is provided in Section 5. Finally, Section 6 concludes the paper.

Problem description

  - Market-Based Resilience Enhancement Approach

The proposed framework contains 3 stakeholders: 1) CLs with load loss reduction requirements; 2) PLs with the capacity of providing fast response resources; 3) DU that serves the customers in the DN including CLs and PLs with resilience enhancement services through trading.

There are 2 sets of games existing in the trading process: 1) games between distinct stakeholders, including the game between CLs and DU, and the game between PLs and DU; 2) games among the same type of stakeholders, including the game between different CLs, and the game between different PLs.

The first set of games is a Stackelberg game, in which DU is the leader, and CLs and PLs are both followers. In the game between DU and CLs, DU firstly selects the strategy and then, CLs find their best response strategies to DU’s strategy. This is also true for the game between DU and PLs. Unlike the traditional Stackelberg game, this set of games in this paper will be iterated to equilibrium.

The second set of games is a non-cooperative and simultaneous game. Unlike the first type, there is no “leader”. All CLs involved in the trading, for example, wish to maximize their own interests. Players in this group have similar goals, yet due to limited information, this group behaves in a limited rational manner in terms of approaching the best strategy. Therefore, this paper uses evolutionary games to simulate such games, where both CLs and PLs can learn from the optimal strategies of individuals in their respective groups to adjust their strategies during the trading process.

Fig.1.  The trading framework of three stakeholders

Finally, to facilitate the participation of all the players to enhance the system resilience, a benefit allocation mechanism has been applied to the proposed framework. In short, the DU organizes the special emergent trading, called resilience enhancement services among the CLs and PLs with extra possibilities also to gain benefits (shared by CLs). To motivate the participation of the PLs, the DU provides awards to the EVs. By contrast, the DU charges an extra to the CLs for providing such an emergency service under adverse events. For the CLs, the economic benefits are from the reduced loss of load. The whole trading framework is as Fig.1.

  - Impact of Typhoon on the Proposed Approach

Faults at different locations in the DN may lead to an isolation of resources, which in turn may have an impact on the trading. The following model is based on typical fault scenarios.

Usually, a typhoon model is built as a sequential trajectory circle model, indicating that the components with different locations in the system are at fault in different periods, as Fig.2 shown. In Fig.2, red circles and green circles represent CLs and PLs respectively, blue circles represent the typhoon in different periods. For example, at time t1, node 8 is likely to be disconnected from the DN, which makes node 8 could not purchase resilience enhancement services. Similarly, at time t5, node 26, a PL, could not sell power if it is “isolated”.

In short, DN faults may physically “isolate” some loads or resources, thus they cannot participate in trading. Therefore, trading in different scenarios should be taken into consideration

Fig.2.  The influence of typhoon on the distribution network

  - Typical Fault Scenarios Considering Typhoon

As mentioned earlier, the number and scale of “isolated” loads and resources vary under different fault scenarios. To accurately describe the faults caused by typhoon, this paper firstly models the typhoon, and analyzes the impact of it on the probability of component faults. Then the most likely scenarios at each period are generated by Monte-Carlo simulation and selected by information entropy constraints, Section III. A describes the mathematical model in detail.

Problem Formulation

  - Typical Fault Scenarios Modelling

3.1.1 Component Fault Rate Considering Weather Conditions: Taking a typical extreme weather typhoon as an example, this paper firstly analyzes the impact of the typhoon on the fault rate of DN components, and secondly selects the set of fault scenarios according to the information entropy constraint.

The typhoon wind field model can be described by , according to [29].

Typhoon is not stationary in practice, it moves on a certain trajectory, and its speed is .

Therefore, the distance of the component from the typhoon center also varies with time, at time t there is:

Transmission lines consist of conductors and towers, and only when both are operating properly at the same time transmission lines do not fail, and under the influence of the typhoon, the fault rate can be calculated as  [30].

The stress received by the conductor and the bending moment applied to the tower is as .

The wind load exerted on the components by a typhoon can be expressed as .

Thus, the distribution line fault rate can be calculated. For example, assuming that c7-27 in Fig.2 consists of M conductors and N towers, the probability of failure of c7-27 is as .

  - Typical Fault Scenario Modelling

A large number of components in the DN makes it necessary to choose scenarios according to the likelihood and uncertainty of their occurrence. Defining the entropy of the DN as .

In this way, typical fault scenarios can be selected based on the actual probability of component fault, and these scenarios must meet the following constraint.

This paper assumes that after a certain period the line fault may be repaired, there is .

Finally, the selection of scenarios needs to be constrained by .

  - “CL-DU-PL” Trading Model Based on Game Theory

In this part, this paper constructs 3 models for 3 stakeholders respectively, as they have different objective functions and constraints.

3.2.1 Model of Critical Loads: The objective function of CLi is .

where  is defined as .

where  is the actual damage function; the second term is the extra payment to the DU, which is a portion of the economic benefit that a CLi obtains by purchasing resilient service to reduce his/her load loss; the third term is the self-supporting part of the resource purchase cost; the fourth term is the resource purchase cost that CLi should pay for upstream users. Obviously, the third and fourth terms are related to the free-riding penalty coefficient (Refer to Fig.4).

is further expressed as a quadratic function with the variable , as  shown.

For gaining more benefits in the game with DU, CLi usually corrects the damage function according to its attributes and willingness when submitting it to DU. In reference [31], Mohammad Shahidehpour et al proposes a method to describe this behavior. He believes that loads can modify the linear term coefficients to “trick” DU about their load importance. This paper adopts the same principle, and the equation  can be replaced by  in the game. Therefore,  can be seen as the game strategy of CLi

The game between CLi and DU is a Stackelberg game, DU is the leader and CLs are followers. When a typhoon comes, DU firstly proclaims the load loss of each CL (pi0,t,s) according to its load importance, then CLs respond with their strategies based on the published information, lastly, DU decides its strategies with each CL (pi,t,s). The above process is a single complete game process, which in practice may be repeated several times for reaching the equilibrium point.

Fig.3.  Critical Load Damage Function & Resource Provision Cost Function

To better describe the strategic equilibrium process of the CL cluster, this paper employs the evolutionary game is used to describe the strategy modification process of CLs, and the specific formula is given in section IV.

The bid curve of CLi can be obtained by differentiating the revised damage function, as Fig.3 shown.

The resilience enhancement service cost is similar to electricity purchase, as .

In fact, this cost is only partly borne by CLi and partly by the downstream users.

Fig.4.  Definition of the free-riding

Definition 1 : The node’s location is defined as downstream in the direction in which the power flow leaves the reference node. Free-riders in this paper are defined only on the set of downstream nodes. With node i as the reference node, the kth downstream node i is the free-rider ik+, and the portion of the service purchase cost that should be allocated to this free-rider is ,  is defined as the free-riding penalty coefficient.

For example, in Fig.4, node i must share the service purchase cost from all his/her upstream nodes, in the figure are respectively i4- to i1-, while allocating its service purchase cost to all downstream nodes. The penalty suffered by node i due to free-riding is

However, it should be noted that as node i could allocate (defined as ) to his/her downstream nodes. Thus, the self-supporting part of the service purchase cost is only . (Refer to )

A trading judgment indicator is established using the difference in load loss before and after CLi participant in the trading.

The DN resilience enhancement index could be constructed by index RIDN [9], E[·] means expected parameter ·.

Constraints are as follows.

indicates rational bidding by CLi;  constrains the economic interests.

3.2.2  Model of Parking Lots: The objective function of PLj is .

could be written as  in detail. The first term of the right side is the actual resource cost function; the second term is the reward to incentive PLj to participant in the trading offered by DU; the last term is the revenue from the sale of its power.

The resource cost function also can be simplified to a quadratic function, as the marginal generation cost.

When submitting this function to DU, similar to the CL side, PLj also modifies this function. Here again, in this paper, this process is described by varying the primary term coefficient.

Also, there is a Stackelberg game existing, the leader is DU, and followers are PLs. Since the entire PL cluster tends to end up with a consistent strategy in order to sell more power, the evaluation game is also applied, similar to CL side.

Unlike , there is no constant term in . The bid curve can be obtained by differentiating .

PLj is able to generate benefits by selling power, as .

Constraints [32]:

means EVs in the PL decide on the resource provision capacity. - restraints the charging and discharging behavior of EVs in emergencies. - restraints the available PLs in contingency conditions.  ensures that all PLs can provide charge and discharge support for the EVs in the system under all circumstances,  constraints that all EVs should enter PL in emergencies,  is utilized to limit the number of EVs in the PL.  then constrains the bidding strategy of PLj.

3.2.3 Model of Distribution Utility: The objective function of DU is .

DU receives a portion of the revenue from CLs and spends a portion of the cost on PLs. And earned the difference from the trading process.

Constraints:

is DN voltage constraint;  is DN power constraint;  ensures minimum profits for DU, in such a circumstance, DU must secure its economic interests before facilitating a  deal. But for other benefit-neutral stakeholders such as DSO, can have no profits.

Solution of the Proposed Model

The games presented in Section III are of pure strategy. As the equilibrium of an evolutionary game is a Nash Equilibrium under pure strategy [33], this paper first calculates CLs and PLs’ evolutionary game equilibrium, then corresponding strategies of them are used as the initial strategies to calculate the equilibrium of the Stackelberg game. If convergence is achieved, equilibrium of the evolutionary game and the Stackelberg game is proved. The proposed solution is shown in Algorithm 1.

Algorithm 1: Solution of the proposed model

1: Step 1 Set the iteration counter ic = 1 and the maximum number of iterations IC, respectively.

2: Step 2 Generate typical fault scenarios based on the predicted typhoon track, then input fixed parameters and initialized

3: Step 3 Do for t=1, 2, …

4: Step 3.1 Calculate CLs and PLs objective functions based on the initial parameters, and update evolutionary game strategies according to (42) and (43).

5: Step 3.2 Determine whether the evolutionary games have reached equilibrium: Yes=Step 3.3, No=Step 3.1.

6: Step 3.3 Solve the DU model with the final strategies in step 3.2 as the initial variables.

7: Step3.4 Determine whether the Stackelberg games have reached equilibrium: Yes=Step 4, No=Step 3.1.

8: Step 4 Set ic=ic+1. If ic ≤ IC go to Step 3, else go to Step 5.

9: Step 5 Output final results.

If the set of strategies selected by a user group is O, define users cluster (CLs or PLs) in this group that chooses strategy y as xy, the whole group utility function is cy,t,s in scenario s at time t when choosing strategy y. xy could switch to strategy z When the utility is better, according to .

The first term of the right side of  is the portion of users who choose other strategies to change to strategy z, the second term is the portion of users who choose strategy z to change to other strategies.

Switching velocity is as .

Case Study

  - Background Data

The modified IEEE 69-bus distribution test system is employed to implement the proposed model [34], as Fig.5. The system contains 4 feeders and 3 tie lines. There are 10 CLs and 5 PLs in the grid. The typhoon trajectory and duration are assumed to be known, constant A=2.34, B=0.7, randC is a random number that matches the standard normal distribution. The duration between two trading in the case study is setting as 30 min, . For other mechanical parameters of the distribution line, refer to [30].

Fig.5.  Modified IEEE 69 node system and the typhoon trajectory

The maximum and minimum SOC values of the battery of EVs are assumed to be 90% and 10%, respectively, while the nominal capacity of batteries considered to be 40 kW·h, the rated charge and discharge capacity of the EVs are considered as 10 kW, the maximum and minimum SOC values of the battery of EVs are assumed to be 90% and 10%, while the charge/discharge efficiency is 85%. And each PL is the equivalent of several adjacent PLs with 30 empty parking spaces. The setting of CLs is shown in Table 1.

Node 65, node 14, node 20, node 42, and node 35 are setting as PL1 to PL5. Gj=0.001, Hj=2.

Pbuy is setting as 0.5$/kW, and Psell is setting as 0.3$/kW. For the free-riding level, only the first three free-riding levels are counted.

Table 1 Critical Load Parameters

| CL | Node | Load (kW) | Quality |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Di | Ei | Fi |
| 1 | 8 | 70 | 0.02 | 2 | 200 |
| 2 | 11 | 145 | 0.02 | 3 | 400 |
| 3 | 21 | 110 | 0.02 | 3 | 400 |
| 4 | 29 | 80 | 0.01 | 2 | 200 |
| 5 | 38 | 380 | 0.03 | 5 | 300 |
| 6 | 39 | 380 | 0.03 | 5 | 300 |
| 7 | 48 | 100 | 0.02 | 3 | 400 |
| 8 | 50 | 600 | 0.04 | 4 | 400 |
| 9 | 53 | 200 | 0.03 | 4 | 300 |
| 10 | 68 | 80 | 0.02 | 2 | 200 |

  - Base Case

In this case, we first calculate all distribution line fault rates in the test system when the typhoon passes by, then fault scenarios are generated from the fault rate. In the simulation result, more than 85% of the scenario’s entropy values are in (5, 25). Thus, Emin/Emax are respectively setting as 5/25. To illustrate our proposed approach more clearly, only the most likely scenarios for each time period are selected in this case, and the scenarios used in this case are shown in Table 2.

Based on these scenarios, trading results are calculated for demonstrating the validity of the proposed model, as Fig.6 and Fig.7 shown (i and j are both setting as 0.5). For the aesthetics of the picture, we use absolute value to make figures for negative objective function values, such as  in Fig.7, and  in Fig.8.

Table 2 Scenarios for base case

| Time | Fault Line | Occurrence Probability |
| --- | --- | --- |
| t0 | None | / |
| t1 | 3-28 | 0.16 |
| t2 | 3-28, 4-36, 37-38 | 0.19 |
| t3 | 37-38, 38-38, 35-39, 9-42 | 0.22 |
| t4 | 9-42, 11-12, 55-56 | 0.12 |
| t5 | 12-13, 16-17 | 0.14 |
| t6 | 15-16, 16-17, 17-18 | 0.20 |
| t7 | 41-69 | 0.08 |
| t8 | 41-69, 68-69 | 0.13 |

Fig.6 could partially demonstrate the validity of the proposed approach, the load loss of CLs can be effectively reduced in almost all scenarios, except when they are isolated. For example, CL1 could reduce load loss by nearly 80% in t1, t2, t3, t6, t7, and t8, but at t4 it can only be reduced by 40%, at t5 it even cannot reduce any loss. In fact, these anomalies occur at t4 and t5 are the results of different network topologies. At time t4, the distribution line breaks between CL1 and PL1, but due to the superior location of CL1 itself, it still could gain a small amount of power supply from other PLs. However, PL1 is isolated at t5, there are not enough resources in the DN and CL1 cannot get any resilient services because it is not “critical” enough. Another example is CL5, its load loss varies nearly twice in different scenarios ($8381.98 at t3, $3738.30 at t8), however, it still can reduce the load loss by 37% even at t3, this type of loads could bring more benefits to DU due to their own attributes, thus, they are considered more “critical” by DU in the trading, i.e. DU will try to minimize their load loss first. In addition, free-riders do get punished in the trading. As neighbors of the most important load CL8 in the DN, CL7 and CL9 could pay less to reduce their load loss, but even then a large part of their cost is free-riding penalties, more details can be seen from Figs in Case 2.

Fig.6.  Trading results of CLs

Fig.7.  Trading results of PLs

Fig.7 has shown the trading results of PLs in the chosen scenarios. In general, due to the limited total amount of resources in the DN, there is no strong competition among PLs. As long as PLs are not isolated, they can gain good economic benefits by participating in the resilience enhancement service. Take PL1 as an example, from t2 to t5, the typhoon has a notable impact on PL1. As the typhoon gradually approaches, the amount of power sold and the benefits obtained by PL1 decrease. For other PLs, such as PL4, the typhoon has few impacts on it, and its trading results in these scenarios are virtually unchanged.

Table 3 Resilience index before and after trading

| Time | Resilience Index RIDN (kW) |  |
| --- | --- | --- |
|  | Before Trading | After Trading |
| t1 | 246.96 | 86.44 |
| t2 | 314.64 | 106.02 |
| t3 | 364.32 | 168.43 |
| t4 | 198.72 | 75.56 |
| t5 | 231.84 | 92.26 |
| t6 | 331.20 | 102.22 |
| t7 | 132.48 | 40.30 |
| t8 | 215.28 | 61.94 |

Table 3 shows the resilience index before and after the trading, it can be seen easily that the resilience of DN has improved greatly after the trading.

The Base Case demonstrates that the market-based approach proposed in this paper can reduce the load loss in emergencies, improve the economic benefits of the three stakeholders, and fully consider the impact of different faults on the trading process. In the next cases, the scenario t8 at in base case is chosen for further study on the economic cost/benefit of the three stakeholders.

  - Case 1: DU Economic Analysis

This case focuses on the impact of the benefit allocation coefficients (i / j) on DU’s economic benefits. We change these two coefficients from 0 to 1 and calculate the objective function value of DU, results are shown in Fig.8.

Fig.8.  Benefit curve of DU

In fact, there are 6 wave crests in the curve in Fig.8, but there is only one maximum point. This means that DU can adjust these two coefficients before trading to maximize its own profit. Likewise, DU can also adjust these two coefficients to reduce its own interests to make other subjects more profitable, thus increasing their willingness to participate in the trading, while it only reaches the optimum in a certain interval. In some practical circumstances, this approach is very flexible and effective. Decreasing i means CLs could pay less to buy the resilience enhancement service, and increasing j means PLs could gain more from the trading, this is important for individuals who focus on their benefits.

Fig.9 is a further refinement of Fig.8, which is two tangent lines from Fig.8. The locations of the 6 crests have been marked in the figure by circles, and five of them are included on the chosen tangent lines. A wave crest means an extreme point within a small interval, and the point (i=0.5, j=0.5) is the maximum point of all wave crests, more wave crests imply more flexibility. For example, when i=0.5 and j changes, there are 3 extreme points on the corresponding tangent (refer to the sub-figure i=0.5), respectively corresponding j=0.1, j=0.5, and j=0.7. The primary goal of DU is to maximize its benefits, and the secondary goal is to facilitate trading. However, these two goals may conflict in some situations, the other two stakeholders also require adequate economic benefits, DU may need to sacrifice a part of its own interests at this point, and this benefit allocation mechanism gives it more flexibility to deal with this situation. For other benefit-neutral stakeholders, this mechanism also makes it easier to achieve their goals.

In short, successful trading requires a balance between the economic interests of all three stakeholders, and this benefit allocation mechanism is designed to do just that, bringing greater flexibility to the trading and making the trading results more controllable.

However, DU is not the only one affected by these two coefficients (i / j), CLs/PLs are also affected by i / j, and their bidding strategies will change when these two coefficients change. Thus, in the next case, the impact of the benefit allocation mechanism on CLs/PLs will be studied.

Fig.9.  Hotspot projection and tangent lines of DU (i =0.5/ j=0.5)

  - Case 2: CLs and PLs Economic Analysis

This case is also running in the same scenario as Case 1 (t8). Fig.10 and Fig.11 are the economic analysis about CLs when the benefit allocation coefficient i changes, Fig.12 is the economic analysis about PLs when the benefit allocation coefficient j changes.

Fig.10.  Economic composition of CL1 when i changes

Fig.10 and Fig.11 are respectively the economic composition of CL1 and CL2 when i changes, and their bidding strategies are also can be seen in figures. In general, as i increasing from 0 to 1, the bidding strategies and the objective function value show a decreasing and then increasing trend, and a few fluctuations appear in the process. It is specified that when i=0 or j=0, the corresponding CL or PL will not participate in the trading. Taking CL1 as an example, it can be seen that the objective function of CL1 consists of four parts, and the penalty of free-riding (the fourth term) accounts for about 10% of its total cost. It is worth noting that CL1’s total cost reduction due to participation in the trading is less than 20% (at t8, form 452.5$ to 390.4$), the impact of the free-riding penalty makes the cost reduction not obvious. To some extent, this can partly prove the effectiveness of the penalty measures proposed in this paper.

The model proposed in this paper places more emphasis on large loads in the trading, large loads are usually more “critical”. Prioritizing large loads not only can obtain more economic benefits, but also leads to more significant resilience improvement of the DN. For example, CL2 could reduce its cost up to 304$ at t8, which is four times CL1. Part of the reason is because of the parameter settings, but the main reason is the load volume gap (CL2 is 145kW, CL1 is 70kW). And since only the first three free-riding levels are calculated in the example, CL2 does not bear the free-riding cost. The larger load could reduce greater load loss in the trading, for CL8, it even could reduce hundreds of dollars at on period, this is another reason for incentivizing the large critical loads to participate in the trading to reduce their load loss.

Fig.11.  Economic composition of CL2 when i changes

Different from the CL side, the economic composition curve and bidding strategy show some similarities of all non-isolated CLs, thus here only PL1 is chosen to illustrate. Fig.12 shows the simulation results, the economic benefits of CL1 first increase and then levels off with 1 increases. The reason for the similarity is maybe the resources in the DN are not sufficient, only all PLs that reach the capacity limit can satisfy the power demand of CLs, thus there is no apparent competitive behavior between PLs. However, the situation becomes distinct when there are sufficient resources in the DN. Well-located PLs sell power more easily and gain more interests, and poorly-located PLs have to lower their bidding strategies. In short, the adequacy of resources in the DN affects the interests of PLs.

Fig.12.  Economic composition of PL1 when j changes

Conclusion and Future works

This paper proposes an emergent trading framework for using parking lots as fast recovery resources to reduce critical load loss and improve the resilience of the entire DN after a typhoon crossing. Under the proposed framework, a mathematical model for the typhoon is built, and a DN fault scenario formation method is proposed. Then an evolutionary Stackelberg game-based trading model is established to consider maximizing all stakeholders’ economic benefits and reducing the load loss. Further, a benefit allocation mechanism and free-riding penalty are introduced in the framework to make it easier to the goal and limit the negative effect of free-riders, with an iterative evolutionary-Stackelberg solution set-up is applied to illustrate the solution of the proposed model. Case studies demonstrate that the proposed framework could reduce critical load loss, and in consequence to improve system resilience. The simulation results also show that by adjusting different parameters related to the benefit allocation mechanism, the proposed framework can be effectively applied to a large range of severity of emergencies.

It should be noted that the current framework considers the free-riding behavior during the emergency trading in a simplified way and cannot fully prevent the negative effect. Therefore, our next step is to further refine the model of free-riding. In addition, the EVs are currently presented by PLs, a finer model of stakeholders such as EV owners will be extended in the future.

References

- M. Panteli, D. N. Trakas, P. Mancarella, and N. D. Hatziargyriou, "Boosting the Power Grid Resilience to Extreme Weather Events Using Defensive Islanding," IEEE Trans. Smart Grid, vol. 7, no. 6, pp. 2913-2922, Nov. 2016.

- X. Liu, M. Shahidehpour, Z. Li, X. Liu, Y. Cao, and Z. Bie, "Microgrids for Enhancing the Power Grid Resilience in Extreme Conditions," IEEE Trans. Smart Grid, vol. 8, no. 2, pp. 589-597, Mar. 2017.

- M. Nazemi, M. Moeini-Aghtaie, M. Fotuhi-Firuzabad, and P. Dehghanian, "Energy Storage Planning for Enhanced Resilience of Power Distribution Networks Against Earthquakes," IEEE Trans. Sustain. Energy, vol. 11, no. 2, pp. 795-806, Apr. 2020.

- M. Yan, Y. He, M. Shahidehpour, X. Ai, Z. Li, and J. Wen, "Coordinated Regional-District Operation of Integrated Energy Systems for Resilience Enhancement in Natural Disasters," IEEE Trans. Smart Grid, vol. 10, no. 5, pp. 4881-4892, Sept. 2019.

- E. Bompard, T. Huang, Y. Wu, and M. Cremenescu, "Classification and Trend Analysis of Threats Origins to the Security of Power Systems ", Int. J. Elec. Power, vol. 50, no. 1, pp. 50-64, Sep. 2013.

- Y. Wang, C. Chen, J. Wang, and R. Baldick, "Research on Resilience of Power Systems Under Natural Disasters—A Review," IEEE Trans. Power Syst., vol. 31, no. 2, pp. 1604-1613, Mar. 2016.

- E. B. Watson and A. H. Etemadi, "Modeling Electrical Grid Resilience Under Hurricane Wind Conditions With Increased Solar and Wind Power Generation," IEEE Trans. Power Syst., vol. 35, no. 2, pp. 929-937, Mar. 2020.

- G. Li, P. Zhang, P. B. Luh, W. Li, Z. Bie, C. Serna, and Z. Zhao, "Risk Analysis for Distribution Systems in the Northeast U.S. Under Wind Storms," IEEE Trans. Power Syst., vol. 29, no. 2, pp. 889-898, Mar. 2014.

- X. Liu, K. Hou, H. Jia, J. Zhao, L. Mili, X. Jin, and D. Wang, "A Planning-Oriented Resilience Assessment Framework for Transmission Systems Under Typhoon Disasters," IEEE Trans. Smart Grid, vol. 11, no. 6, pp. 5431-5441, Nov. 2020.

- T. Ding, M. Qu, Z. Wang, B. Chen, C. Chen, and M. Shahidehpour, "Power System Resilience Enhancement in Typhoons Using a Three-Stage Day-Ahead Unit Commitment," IEEE Trans. Smart Grid, vol. 12, no. 3, pp. 2153-2164, May. 2021.

- M. Panteli, D. N. Trakas, P. Mancarella, and N. D. Hatziargyriou, “Boosting the power grid resilience to extreme weather events using defensive islanding,” IEEE Trans. Smart Grid, vol. 7, no. 6, pp. 2913–2922, Nov. 2016.

- G. Huang, J. Wang, C. Chen, J. Qi, and C. Guo, "Integration of Preventive and Emergency Responses for Power Grid Resilience Enhancement," IEEE Trans. Power Syst., vol. 32, no. 6, pp. 4451-4463, Nov. 2017.

- J. Liu, C. Qin, and Y. Yu, "Enhancing Distribution System Resilience With Proactive Islanding and RCS-Based Fast Fault Isolation and Service Restoration," IEEE Trans. Smart Grid, vol. 11, no. 3, pp. 2381-2395, May. 2020.

- P. Jamborsalamati, M. J. Hossain, S. Taghizadeh, G. Konstantinou, M. Manbachi, and P. Dehghanian, "Enhancing Power Grid Resilience Through an IEC61850-Based EV-Assisted Load Restoration," IEEE Trans. Ind. Informat, vol. 16, no. 3, pp. 1799-1810, Mar. 2020. (you)

- W. Chen, Y. Shi, Y. Chen, Y. Li, C. Guo, C. Yang, and Y. Shen, "Robust Islanded Restoration Coordinating Multiple Distributed Resources to Enhance Resilience of Active Distribution System," in IEEE Power Energy Soc. Gen. Meet. (PESGM), Atlanta, GA, United States, 2019, pp. 1-5.

- A. Gholami, T. Shekari, F. Aminifar, and M. Shahidehpour, "Microgrid Scheduling With Uncertainty: The Quest for Resilience," IEEE Trans. Smart Grid, vol. 7, no. 6, pp. 2849-2858, Nov. 2016.

- T. Ding, Z. Wang, W. Jia, B. Chen, C. Chen, and M. Shahidehpour, "Multiperiod Distribution System Restoration with Routing Repair Crews, Mobile Electric Vehicles, and Soft-Open-Point Networked Microgrids," IEEE Trans. Smart Grid, pp. 4795-4808, Nov. 2020.

- E. Kianmehr, S. Nikkhah, V. Vahidinasab, D. Giaouris, and P. C. Taylor, "A Resilience-Based Architecture for Joint Distributed Energy Resources Allocation and Hourly Network Reconfiguration," IEEE Trans. Ind. Informt., vol. 15, no. 10, pp. 5444-5455, Oct. 2019.

- H. Gao, Y. Chen, S. Mei, S. Huang, and Y. Xu, "Resilience-Oriented Pre-Hurricane Resource Allocation in Distribution Systems Considering Electric Buses," Proc. IEEE, vol. 105, no. 7, pp. 1214-1233, Jul. 2017.

- H. Shin and R. Baldick, "Plug-In Electric Vehicle to Home (V2H) Operation Under a Grid Outage," IEEE Trans. Smart Grid, vol. 8, no. 4, pp. 2032-2041, Jul. 2017.

- Z. Yang, P. Dehghanian, and M. Nazemi, "Seismic-Resilient Electric Power Distribution Systems: Harnessing the Mobility of Power Sources," IEEE Tran. Ind. Appl., vol. 56, no. 3, pp. 2304-2313, May-June. 2020.

- C. Wu, H. Mohsenian-Rad, and J. Huang, "Vehicle-to-Aggregator Interaction Game," IEEE Trans. Smart Grid, vol. 3, no. 1, pp. 434-442, Mar. 2012.

- J. Ma, J. Deng, L. Song, and Z. Han, "Incentive Mechanism for Demand Side Management in Smart Grid Using Auction," IEEE Trans. Smart Grid, vol. 5, no. 3, pp. 1379-1388, May. 2014.

- Y. Wu, Z. Lin, C. Liu, Y. Chen and N. Uddin, "A Bargaining Strategy-based Game Model of Power Demand Response Considering Hydrogen-to-Electricity Conversion of Industrial Users," IEEE Trans. Ind. Appl., Jun. 2021.

- D. Kim and J. Kim, "Design of Emergency Demand Response Program Using Analytic Hierarchy Process," IEEE Trans. Smart Grid, vol. 3, no. 2, pp. 635-644, Jun. 2012.

- Y. Guo, H. Li, and M. Pan, "Colocation Data Center Demand Response Using Nash Bargaining Theory," IEEE Trans. Smart Grid, vol. 9, no. 5, pp. 4017-4026, Sept. 2018.

- Y. Dong, X. Xie, K. Wang, B. Zhou, and Q. Jiang, "An Emergency-Demand-Response Based Under Speed Load Shedding Scheme to Improve Short-Term Voltage Stability," IEEE Trans. Power Syst. vol. 32, no. 5, pp. 3726-3735, Sept. 2017.

- S. M. Abedi, and M. R. Haghifam, "CDF-based reliability insurance contracts considering free-riding," Int. J. Elect. Power Energy Syst., vol. 53, pp. 949–955, Dec. 2013.

- B. M. E., S. Emil, and R. L. R., "Hurricane Wind Speeds in the United States," J. Struct. Div., vol. 106, no. 10, pp. 2001-2016, Oct. 1980.

- M. Panteli, C. Pickering, S. Wilkinson, R. Dawson, and P. Mancarella, "Power System Resilience to Extreme Weather: Fragility Modeling, Probabilistic Impact Assessment, and Adaptation Measures," IEEE Trans. Power Syst., vol. 32, no. 5, pp. 3747-3757, Sept. 2017.

- R. Mohammadi, H. R. Mashhadi, and M. Shahidehpour, "Market-Based Customer Reliability Provision in Distribution Systems Based on Game Theory: A Bi-Level Optimization Approach," IEEE Trans. Smart Grid, vol. 10, no. 4, pp. 3840-3848, Jul. 2019.

- M. Zhou, Z. Wu, J. Wang, and G. Li, "Forming Dispatchable Region of Electric Vehicle Aggregation in Microgrid Bidding," IEEE Trans. Ind. Inform., vol. 17, no. 7, pp. 4755-4765, Jul. 2021.

- L. Tadj and A. Touzene, "A QBD approach to evolutionary game theory," Appl. Math. Model., vol. 27, no. 11, pp. 913-927, Nov. 2003.

- M. E. Baran and F. F. Wu, "Optimal capacitor placement on radial distribution systems", IEEE Trans. Power Deliv., vol. 4, no. 1, pp. 725-734, Jan. 1989.